# Automatic-filter type 6.19

Filtration and the fully automatic backflushing are based on the bipolar functioanal principle.

The conatminated fluid enters from both sides into the inside of the candle.

By this, the the particles of contamination are retained over the whole length of the candle.

So, the entire filtartion area is uniformly used.

The differential or time dependend regeneration of the filter is iniciated without interruption of operation.

The two-sided open candle and a rotating flushing arm effectuate a axial– and

cross-backflushing to the point and distribution of the backflush energy on the entire lenght of the filter-candle.

The automatic filter is a ready to work filter unit.

The mud drain valve can optional actuated pneumatically or hydraullically.

The electronic control box belongs to the Standard equipment.

Type 6.19 automatic filter:

Size / nominal diameter:			DN 300

Housing material:				cast iron

Internal parts:					stainless steel

Kind of filter-candle:				two-sided open cylindrical candle

Type of filter-candle:				Cross-, longitudinal or mesh-candle

Candle quantity:				92 pcs.

Filter area:					32396 cm²

Operational data:

Medium:					...... – water

Flow rate:					max. 1020 m³/h

Allowable operation – pressure:		1 – 10 bar  (higher operation-pressure on request)

Allowable operation – temperature:		0 – 60°C

Grade of filtration:				150 micron

Backflush – medium:	External medium: (up to DN 300):   0,63 l/s

Power supply:					400V, 50 Hz

Manufacturer: 				Boll & Kirch Filterbau GmbH

Type:						Selfclean 6.19